## Sheet1
Work Element Description | Unit | Man-hours per Unit
Pipe Diameter in Inches
|  | up to 1 | 1 1/4 | 1 1/2 | 2 | 2 1/2 | 3 | 3 1/2 | 4 | 5 | 6 | 8
22 11 13.23 Copper Pipe
Type K tubing | LF | (0010) 0.1610 | (0020) 0.2660
Type L tubing | LF | (0030) 0.1570 | (0040) 0.1840 | (0050) | (0060) | (0070) | (0080) | (0090) | (0100) | (0110) | (0120) | (0130)
|  |  |  | 0.2050 | 0.2530 | 0.3430 | 0.3800 | 0.4950 | 0.5450 | 0.6260 | 0.7980 | 0.8870
Type drain, waste, and vent (DWV) tubing | LF |  | (0140) 0.1770 | (0150) 0.1970 | (0160) 0.2420 |  | (0170) |  | (0180) | (0190) | (0200)
[7 empty] | 0.3670 |  | 0.5320 | 0.5900 | 0.7590
Minimum suggested crew size: one utilitiesman and one laborer.
Notes: 1. Used for facility water distribution piping. 2. Use a 1.15 multiplier for silver solder joints (air conditioning and refrigeration only). 3. The installation of copper pipe includes cutting; cleaning and soldering joints; plumbing and grading pipe; and installing pipe hangers and straps. 4. Types of copper pipe: a. K—A thick-walled, flexible copper tubing. A thicker wall than type L and M. required for underground installations. Typical uses include water services, plumbing, heating, steam, gas, oil, oxygen, and other applications where thick-walled tubing is required. Can be used with sweat, flared, and compression fittings. b. L—Standard tubing used for interior, above ground plumbing. Uses include heating, air conditioning, steam, gas, oil, and underground drainage lines. Only sweat and flare fittings are legal for gas lines. 5. DWV. It is recommended for above ground use only and no pressure applications. Sweat fittings only.