## Sheet1
Work Element Description | Unit | Man-hours per Unit
26 05 00 Common Work Results for Electrical
(0010) Construct H-frame and install three-phase transformer bank | Each | 132.0
String Primary Conductors
(0020) American Wire Gage (AWG) #6 to AWG #1 bare copper | LF | 0.0160
(0030) AWG #0 to AWG #0000 bare copper | LF | 0.0232
(0040) Larger than AWG #0000 bare copper | LF | 0.0238
Install Transformer on Poles
(0050) Single transformer 10 to 75 kilovolt-ampere (kVA) | Each | 12.0
(0060) Three single-phase transformers 10 to 75 kVA | Bank | 16.0
Install secondary racks | Each | 2.4
Install Secondary Conductors and Service Drops
(0080) AWG #4 and smaller: four-wire, weatherproof | LF | 0.0530
(0090) AWG #2 to AWG # 0: four-wire, weatherproof | LF | 0.0690
Install Voltage Regulators
(0100) 25 kVA, single-phase, pole mounted | Each | 17.60
(0110) 75 to 125 kVA, three-phase, slab mounted | Each | 81.60
(0120) Capacitor units, pole mounted, factory preassembled, all kVA ratings | Each | 16.80
Install Primary Protective Devices
(0130) Pole top air break switches, three poles | Each | 43.20
(0140) Enclosed-fused disconnect switch | Each | 8.0
(0150) Open-fused disconnect switch | Each | 8.0
Minimum suggested crew size: Capacitor units: two linemen and one ground man H-frame: six electricians Install primary protective devices: four electricians Install secondary conductors and service Drop #4 and smaller: two electricians Install secondary conductors and service Drop #2 to #0: two electricians, one equipment operator Install secondary racks: two electricians Install transformers on poles: three electricians, one equipment operator Install voltage regulators: three electricians Install wire guys: three electricians String primary conductors: ten electricians, one equipment operator Single cross assembly installation: two electricians.
Notes: 1. Cross arm assembly figures are based on work being done before pole is set. If work must be done after pole is set, use 1.15 multiplier. 2. When using bucket truck, use 0.85 multiplier.