## Sheet1
Work Element Description | Unit | Man-hours per Unit
26 05 13.00 Medium-Voltage Cables
Excavate trench for duct or direct burial of cable
(0010) Hand excavating | CYD | 13.60
(0020) Machine excavating | LF | 0.0110
Install 4-inch-diameter conduit in trench, rigid galvanized steel (0030) One conduit without concrete (includes terminations and fittings) | LF
0.240
(0040) Underground duct bank | LF | 0.1330
Install direct burial cable in trench
(0050) Up to AWG #0 1/0—three conductors | LF | 0.0860
(0060) AWG #00 2/0 to 500 MCM—three conductors | LF | 0.1790
Pull cable into duct
(0070) AWG #6—three conductors | LF | 0.0580
(0080) AWG #2—three conductors | LF | 0.110
(0090) AWG #0000 4/0—three conductors | LF | 0.1950
(0100) 500 MCM—four conductors | LF | 0.350
Pull cable into duct underground service to building
(0110) AWG #2—four conductors | LF | 0.1440
(0120) AWG #0—four conductors | LF | 0.2240
Minimum suggested crew size: two electricians.
Notes: 1. All excavating is figured on average soil conditions. 2. Duct man-hour figures allow for a normal number of bends, bells, and fittings, and installing pull line. 3. Direct burial cable in trench requires a sand bed. 4. Concrete encasement under roadway requires reinforcing steel. 5. When using mechanical cable-puller, use 0.85 multiplier.
Legend: MCM = one thousand circular mils